## Sheet1
默认IP地址192.168.1.10，端口503，通信协议ModbusTCP/IP
| 名称 | Parameter name | 地址 | 数据类型
1 | 功率 | Power | 3514 | 16位有符号整形 | 16-bit Signed Plastic
2 | 转速 | Speed | 3515 | 16位有符号整形 | 16-bit Signed Plastic
3 | 缸温1 | Cylinder temperature 1 | 3001 | 浮点型 | float
4 | 缸温2 | Cylinder temperature 2 | 3003 | 浮点型 | float
5 | 缸温3 | Cylinder temperature 3 | 3005 | 浮点型 | float
6 | 缸温4 | Cylinder temperature 4 | 3007 | 浮点型 | float
7 | 缸温5 | Cylinder temperature 5 | 3009 | 浮点型 | float
8 | 缸温6 | Cylinder temperature 6 | 3011 | 浮点型 | float
9 | 缸温7 | Cylinder temperature 7 | 3013 | 浮点型 | float
10 | 缸温8 | Cylinder temperature 8 | 3015 | 浮点型 | float
11 | 缸温9 | Cylinder temperature 9 | 3017 | 浮点型 | float
12 | 缸温10 | Cylinder temperature 10 | 3019 | 浮点型 | float
13 | 缸温11 | Cylinder temperature 11 | 3021 | 浮点型 | float
14 | 缸温12 | Cylinder temperature 12 | 3023 | 浮点型 | float
15 | 缸温13 | Cylinder temperature 13 | 3025 | 浮点型 | float
16 | 缸温14 | Cylinder temperature 14 | 3027 | 浮点型 | float
17 | 缸温15 | Cylinder temperature 15 | 3029 | 浮点型 | float
18 | 缸温16 | Cylinder temperature 16 | 3031 | 浮点型 | float
19 | 排温1 | Exhaust temperature 1 | 3041 | 浮点型 | float
20 | 排温2 | Exhaust temperature 2 | 3043 | 浮点型 | float
21 | 排温3 | Exhaust temperature 3 | 3045 | 浮点型 | float
22 | 排温4 | Exhaust temperature 4 | 3047 | 浮点型 | float
23 | 排温5 | Exhaust temperature 5 | 3049 | 浮点型 | float
24 | 排温6 | Exhaust temperature 6 | 3051 | 浮点型 | float
25 | 排温7 | Exhaust temperature 7 | 3053 | 浮点型 | float
26 | 排温8 | Exhaust temperature 8 | 3055 | 浮点型 | float
27 | 排温9 | Exhaust temperature 9 | 3057 | 浮点型 | float
28 | 排温10 | Exhaust temperature 10 | 3059 | 浮点型 | float
29 | 排温11 | Exhaust temperature 11 | 3061 | 浮点型 | float
30 | 排温12 | Exhaust temperature 12 | 3063 | 浮点型 | float
31 | 排温13 | Exhaust temperature 13 | 3065 | 浮点型 | float
32 | 排温14 | Exhaust temperature 14 | 3067 | 浮点型 | float
33 | 排温15 | Exhaust temperature 15 | 3069 | 浮点型 | float
34 | 排温16 | Exhaust temperature 16 | 3071 | 浮点型 | float
35 | 水温 | water temperature | 3105 | 浮点型 | float
36 | 油温 | Oil temperature | 3107 | 浮点型 | float
37 | 补偿温度 | Compensation temperature | 3109 | 浮点型 | float
38 | 滤前油压 | Oil pressure before filter | 3111 | 浮点型 | float
39 | 滤后油压 | Oil pressure after filter | 3113 | 浮点型 | float
40 | 增压器油压1 | Turbocharger oil pressure1 | 3115 | 浮点型 | float
41 | 发电量 | Total power output | 3117 | 32位有符号整形 | 32-bit signed plastic
42 | 运行时间 | Running time | 3119 | 32位有符号整形 | 32-bit signed plastic
43 | 燃气阀开度 | Gas valve position | 3121 | 浮点型 | float
44 | 节气门开度1 | Throttle position 1 | 3129 | 浮点型 | float
45 | U相绕组温度 | U-phase winding temperature | 3139 | 浮点型 | float
46 | V相绕组温度 | V-phase winding temperature | 3141 | 浮点型 | float
47 | W相绕组温度 | W-phase winding temperature | 3143 | 浮点型 | float
48 | 驱动端轴承温度 | Drive end bearing temperature | 3145 | 浮点型 | float
49 | 自由端轴承温度 | Free end bearing temperature | 3147 | 浮点型 | float
50 | 功率因素 | Power factor | 3149 | 浮点型 | float
51 | SRO | SRO | 3151 | 浮点型 | float
52 | VRO | VRO | 3153 | 浮点型 | float
53 | MAP1 | Manifold Pressure 1 | 3159 | 浮点型 | float
54 | MAT1 | Manifold Temperature 1 | 3161 | 浮点型 | float
55 | MAP2 | Manifold Pressure 2 | 3163 | 浮点型 | float
56 | MAT2 | Manifold Temperature 2 | 3165 | 浮点型 | float
57 | Lambda | Lambda | 3169 | 浮点型 | float
58 | 燃气压差 | Pressure Difference Before and After Gas Valve | 3175 | 浮点型 | float
59 | 燃气压力 | Gas Pressure | 3177 | 浮点型 | float
60 | 燃气温度 | Gas temperature | 3179 | 浮点型 | float
61 | 机油滤压差 | Differential oil filter pressure | 3187 | 浮点型 | float
62 | 节气门开度2 | Throttle position 2 | 3193 | 浮点型 | float
63 | 曲轴箱压力 | Crankcase pressure | 3195 | 浮点型 | float
64 | 左增压器前压力 | Left Turbocharger front pressure | 3197 | 浮点型 | float
65 | 右增压器前压力 | Right Turbocharger front pressure | 3199 | 浮点型 | float
66 | 节气门前压力1 | Pre-throttle pressure1 | 3201 | 浮点型 | float
67 | 蓄电池电压 | Battery voltage | 3203 | 浮点型 | float
68 | 点火提前角 | Ignition advance angle | 3205 | 浮点型 | float
69 | 节气门前压力2 | Pre-throttle pressure 2 | 3207 | 浮点型 | float
70 | 增压器油压2 | Turbocharger oil pressure2 | 3209 | 浮点型 | float
71 | 燃气管道压力 | Gas line pressure | 3211 | 浮点型 | float
72 | 涡前排温1 | Exhaust temperature before turbocharger 1 | 3221 | 浮点型 | float
73 | 涡前排温2 | Exhaust temperature before turbocharger 2 | 3223 | 浮点型 | float
74 | 旁通阀开度 | Bypass valve position | 3233 | 浮点型 | float
75 | 高温三通阀开度 | High temperature three-way valve position | 3235 | 浮点型 | float
76 | 低温三通阀开度 | Low temperature three-way valve position | 3237 | 浮点型 | float
77 | 涡后排温1 | Exhaust temperature after turbocharger 1 | 3239 | 浮点型 | float
78 | 涡后排温2 | Exhaust temperature after turbocharger 2 | 3241 | 浮点型 | float
79 | UV相电压 | UV phase voltage | 3504 | 16位无符号整形 | 16-bit Unsigned Plastic
80 | VW相电压 | VW phase voltage | 3505 | 16位无符号整形 | 16-bit Unsigned Plastic
81 | WU相电压 | WU phase voltage | 3506 | 16位无符号整形 | 16-bit Unsigned Plastic
82 | U相电流 | U-phase current | 3507 | 16位无符号整形 | 16-bit Unsigned Plastic
83 | V相电流 | V-phase current | 3508 | 16位无符号整形 | 16-bit Unsigned Plastic
84 | W相电流 | W phase current | 3509 | 16位无符号整形 | 16-bit Unsigned Plastic
85 | 母线电压AB | Busbar voltage AB | 3510 | 16位无符号整形 | 16-bit Unsigned Plastic
86 | 母线电压BC | Busbar voltage BC | 3511 | 16位无符号整形 | 16-bit Unsigned Plastic
87 | 母线电压CA | Bus voltage CA | 3512 | 16位无符号整形 | 16-bit Unsigned Plastic
88 | 功率设定 | Power setting | 640 | 16位有符号 | 16-bit signed
89 | 机组启动 | Unit startup | 191.0 | BOOL | 读写/Read and Write
90 | 机组停机 | Unit shutdown | 191.1 | BOOL | 读写/Read and Write
91 | 报警消音 | Alarm Silencing | 191.2 | BOOL | 读写/Read and Write
92 | 故障复位 | Fault reset | 191.3 | BOOL | 读写/Read and Write
93 | 合分闸 | Closing and Opening | 191.4 | BOOL | 读写/Read and Write